QUESTIONS AFTER CHINESE CHANGES ON THE P&ID (26.03.2026)

- Chinese designer has applied changes on P&ID_v2, while our latest and updated version of the diagram is v3. I have applied changes to our latest v3 diagram, with new date, without revision change.

- The process data updated by the Chinese designer in the tables, differ from our latest data. I kept our latest data without applying Chinese ones. IMPORTANT

- Insulation is added for B6505~6511 and B6512, according to our latest insulation considerations.

- I applied all changes depicted in the Chinese designer diagram to ours:

  - added vent connection and valve from B6200 to the dryer duct

  - removed reducers on all condensate outlet lines

  - updated configuration of condensate outlet lines from W6504 1~3

  - updated configuration of steam lines to W6504 1~3

  - updated configuration of W6503 A/B inlet and outlet lines

  - changed the vent size of the tank to DN150 and updated its connection configuration to W6504-1 inlet

  - relocated F6500 after of W6501 and moved out-of-scope PDT-A101 accordingly

  - removed air louvre (don't we need to have a coarse air filter at the air intake for any large debris?)

  - changed the expanded air inlet intake part of the heater according to Chinese diagram

  - changed line size, after reducer at DN40 up to FT-C101 and after it, on condensate outlet line of W6503 A (it is marked as DN65 at the outgoing line before the tie-in point)

  - added access hatches to B6505~6511 with GSs

Should I update the Valve List with new revision following above changes?

Please let me know if all changes above are alright and if I have missed any item.

Regards,

Ali