## Instrument Index
INSTRUMENT LIST AND SPECIFICATION
MODIFIED STARCH DRYING PROJECT – AGRANA – ROMANIA
PROJECT No. : 5204 | [28 empty] | REV.: | DATE: | [5 empty] | SPECIFIED BY: | CHECKED BY: | APPROVED BY:
REFER P&ID No.: 5204-PR-DW-0001-03 | [28 empty] | 0 | 02.01.2026 | [5 empty] | A.H. | P.S. | A.Z.
DOCUMENT No: 5204-IN-SP-0001-02 | [28 empty] | 1 | 04.02.2026 | [5 empty] | A.H. | P.S. | A.Z.
[29 empty] | 2 | 28.03.2026 | [5 empty] | A.H. | P.S. | A.Z.
ITEM No. | TAG No. | QUANTITY | FUNCTION | LOCATION | LINE No. | SERVICE 1 | SERVICE 2 | LINE SIZE | DESCRIPTION | INSTRUMENT TYPE | I/O TYPE | MEDIA | OPERATING |  | DESIGN |  | MEDIA PHASE (S/L/G) | PROCESS CONNECTION | THERMOWELL INSERTION | POWER SUPPLY | SIGNAL TYPE | DIAL / CALIBRATED RANGE | SENSOR / INSTRUMENT RANGE | UNIT | SIGNAL PASSIVE / ACTIVE | ELECTRICAL CONNECTION | JB No. | MULTIPLE CABLE TAG | SIGNAL |  | SET POINT | ALARM SET POINTS |  |  |  | MATERIAL | MANUFACTURER | HAZARDOUS CLASSIFICATION | MODEL No. | CATALOGUE No. | REMARKS
[13 empty] | TEMP. (°C) | PR. (barg) | TEMP. (°C) | PR. (barg) | [12 empty] | SOURCE | TO |  | LL | L | H | HH
1 | WT-B6200 | 4 | Instrument | Common Area | – | B6200 Weighing System | B6200 | – | Weighing Transmitter | Load Cell and Transmitter | AI | Wet Starch Cake | Amb. | – | Amb. | – | S | Mounted | – | 24 DC | 4-20 mA |  | TBD | kg | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | Mettler Toledo | N/A | STD | Mettler Toledo IND560 + Load Cell set
2 | PT-S101 | 1 | Instrument | Common Area | Steam Header | Steam | – | DN 150 | Pressure Transmitter |  | AI | Steam | 189 | 11 | 220 | 16 | G | 1/2" NPT | – | Loop | 4-20 mA | 0–16 | 0 – 16 | barg | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | PMC71B | PMC51B-AA21A2B1A | PMC71B: is used instead of PMP51B in Aschach; max. temp. for PMP51B is 125°C -> diaphragm seal necessary but not found in specification; communication with Bluetooth not an option too? Standard in Aschach is ISO228 G not 1/2" NPT, stainless steel TAG-plate missing; check type if installation in hygienic area
3 | TT-S101 | 1 | Instrument | Common Area | Steam Header | Steam | – | DN 150 | Temperature Transmitter | RTD + TX | AI | Steam | 189 | 11 | 220 | 16 | G | 1/2" NPT | Yes | Loop | 4-20 mA | 0–210 | 0–220 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B | TM131: standard in Aschach is G1/2 316L/Ti (process connection), iTherm Strong Sens +500°, 4-wire, with Bluetooth and stainless steel TAG-plate; in hygienic areas iTherm 411 with process connection acc. DIN 11851 with TMT72 4-wire and Bluetooth is used
4 | FT-S101 | 1 | Instrument | Common Area | Steam Header | Steam | – | DN 150 | Flow Transmitter | Vortex Flow Meter | AI | Steam | 189 | 11 | 220 | 16 | G | Flanged | – | 24 DC | 4-20 mA | 0-1000 | 0-1200 | kg/hr | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | Prowirl F200 | 7F2B-DN125AA21A1B (Bluetooth-enabled vortex) | FT S101 acc. P&ID and list DN150 but specification 7F2C1H is DN100; standard in Aschach is 4-20mA+Imp./Frequ./Switch, 4-lins display, touch and split version
5 | PG-S101 | 1 | Instrument | Common Area | – | Steam | – | DN 125 | Pressure Gauge | Pressure Gauge | AI | Steam | 189 | 11 | 220 | 16 | G | Threaded | – | – | Local |  | 0–12 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | N/A | Bourdon | WIKA 213.53 SS316
6 | TT-C101 | 1 | Instrument | Common Area | – | Condensate | W6501 | DN 65 | Temperature Transmitter | RTD + TX | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Flanged | Yes | Loop | 4–20 mA |  | 0–220 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
7 | PG-C101 | 1 | Instrument | Common Area | – | Condensate | W6501 | DN 65 | Pressure Gauge | Pressure Gauge | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Threaded | – | – | Local |  | 0–12 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | N/A | Bourdon | WIKA 213.53 SS316 | Pressure gauge: according EN 837-1, materials ?, class 1, shut-off device where included? WIKA is okay
8 | TT-C102 | 1 | Instrument | Common Area | – | Condensate | W6504-1/2 | DN 65 | Temperature Transmitter | RTD + TX | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Flanged | Yes | Loop | 4–20 mA |  | 0–220 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
9 | PG-C102 | 1 | Instrument | Common Area | – | Condensate | W6504-1/2 | DN 65 | Pressure Gauge | Pressure Gauge | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Threaded | – | – | Local |  | 0–12 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | N/A | Bourdon | WIKA 213.53 SS316
10 | TT-C103 | 1 | Instrument | Common Area | – | Condensate | W6504-4/5/6 | DN 65 | Temperature Transmitter | RTD + TX | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Flanged | Yes | Loop | 4–20 mA |  | 0–220 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
11 | PG-C103 | 1 | Instrument | Common Area | – | Condensate | W6504-4/5/6 | DN 65 | Pressure Gauge | Pressure Gauge | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Threaded | – | – | Local |  | 0–12 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | N/A | Bourdon | WIKA 213.53 SS316
12 | LT-B6515 | 1 | Instrument | Common Area | – | Condensate | B6515 | – | Level Transmitter | Radar Level TX | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Flanged | – | Loop | 4–20 mA |  | 0–H | m | PASSIVE |  |  |  | FLD | CR | [6 empty] | E + H | N/A | FMR67 | FMR67-AAABBB21A1B (Bluetooth-enabled radar)
13 | TG-B6515 | 1 | Instrument | Common Area | – | Condensate | B6515 | – | Temperature Gauge | Temperature Gauge |  | Condensate | 170-189 |  | 220 | 16 | L | Flanged | Yes | – | Local |  | 0–200 | °C | PASSIVE | [10 empty] | SS 316L | EU | N/A | Bimetal | Bimetal 0–200°C | Temperature gauge: no further details specified, WIKA is okay
14 | PG-P6501 | 1 | Instrument | Common Area | – | Condensate | P6501 | DN 40 | Pressure Gauge | Pressure Gauge |  | Condensate | 90 | 3 | 200 | 10 | L | Threaded | – | – | Local |  | 0–10 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | N/A | Bourdon | WIKA 213.53 SS316
15 | TT-C104 | 1 | Instrument | Common Area | – | Condensate | W6503 A | DN 40 | Temperature Transmitter | RTD + TX | AI | Condensate | 170-189 | 8-11 | 220 | 16 | L | Flanged | Yes | Loop | 4–20 mA |  | 0–220 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
16 | FT-C101 | 1 | Instrument | Common Area | Condensate Header | Condensate | W6503 A | DN 40 | Flow Transmitter | Vortex Flow Meter | AI | Condensate | 90 | 3 | 200 | 10 | L | Flanged | – | Loop | 4–20 mA |  | Vendor | m³/hr | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | Prowirl F200 | 7F2B-DN40AA21A1B
17 | TG-A101 | 1 | Instrument | Common Area | Air Heater | Ambient Air | Air Intake | – | Temperature Gauge | Temperature Gauge | – | Air | -30/+50 | 0-1 | -40/+60 | – | G | Mounted | – | – | Local | -30/+50 |  | °C | PASSIVE | [10 empty] | SS 316L | EU | N/A | Bimetal | Bimetal 0–200°C
18 | TT-A102 | 1 | Instrument | Common Area | Air Heater | Hot Air | W6501 | – | Temperature Transmitter | RTD + TX | AI | Hot Air | 50-160 | 0.5-1 | 200 | 2 | G | Threaded | – | Loop | 4–20 mA |  | 0 - 200 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
19 | PT-A101 | 1 | Instrument | Common Area | Air Heater | Hot Air | F6502 | – | Pressure Transmitter | Pressure TX | AI | Hot Air | 50-160 | 0.5-1 | 200 | 2 | G | 1/2" NPT | – | Loop | 4–20 mA |  |  | barg | PASSIVE |  |  |  | FLD | CR | [6 empty] | E + H | N/A | PMC71B | PMC51B-AA21A2B1A
20 | PT-A102 | 1 | Instrument | Common Area | Air Heater | Hot Air | F6502 | – | Pressure Transmitter | Pressure TX | AI | Hot Air | 50-160 | 0.5-1 | 200 | 2 | G | 1/2" NPT | – | Loop | 4–20 mA |  |  | barg | PASSIVE |  |  |  | FLD | CR | [6 empty] | E + H | N/A | PMC71B | PMC51B-AA21A2B1A
21 | TG-A102 | 1 | Instrument | Common Area | Air Heater | Hot Air | W6503 A/B | – | Temperature Gauge | Temperature Gauge | – | Air | 160 | 0.5-1 | 200 | – | G | Mounted | Yes | – | Local |  | 0 - 200 | °C | PASSIVE | [10 empty] | SS 316L | EU | N/A | Bimetal | Bimetal 0–200°C
22 | TG-A103 | 1 | Instrument | Common Area | Air Heater | Hot Air | W6504-1/2/3 | – | Temperature Gauge | Temperature Gauge | – | Air | 160 | 0.5-1 | 200 | – | G | Mounted | Yes | – | Local |  | 0 - 200 | °C | PASSIVE | [10 empty] | SS 316L | EU | N/A | Bimetal | Bimetal 0–200°C
23 | TT-101 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Temperature Transmitter | RTD + TX | AI | Hot Air | 170 | 0.5-1 | 220 | 2 | G | Threaded | Yes | Loop | 4–20 mA |  | 0 - 200 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | N/A | TR10 + TMT | TMT182B-AAA1A1AA1B
24 | TG-101 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Temperature Gauge | Temperature Gauge | – | Hot Air | 170 | 0.5-1 | 220 | – | G | Mounted | Yes | – | Local | 0-200 | 0 - 200 | °C | PASSIVE | [10 empty] | SS 316L | EU | N/A | Bimetal | Bimetal 0–200°C
25 | TG-102 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Temperature Gauge | Temperature Gauge | – | Hot Air | 160 | 0-1 | 200 | – | G | Mounted | Yes | – | Local |  | 0 - 200 | °C | PASSIVE | [10 empty] | SS 316L | EU | Zone 20 | Bimetal | Bimetal 0–200°C
26 | TT-102 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Temperature Transmitter | RTD + TX | AI | Hot Air | 160 | 0-1 | 200 | 2 | G | Threaded | Yes | Loop | 4–20 mA |  | 0 - 200 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | TR10 + TMT | TMT182B-AAA1A1AA1B
27 | PG-102 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Pressure Gauge | Pressure Gauge | – | Hot Air | 160 | 0-1 | 200 | 2 | G | Threaded | – | – | Local |  | 0 - 2 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | Zone 20 | Bourdon | WIKA 213.53 SS316
28 | PT-102 | 1 | Instrument | Common Area | Dryer Duct | Hot Air | – | – | Pressure Transmitter | Pressure TX | AI | Hot Air | 160 | 0-1 | 200 | 2 | G | 1/2" NPT | – | Loop | 4–20 mA |  | 0 - 2 | barg | PASSIVE |  |  |  | FLD | CR | [6 empty] | E + H | Zone 20 | PMC71B | PMC51B-AA21A2B1A
29 | GS-101 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | Air Heater | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | N/A | STD | Honeywell Burst Sensor BES-EX
30 | GS-102 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | Air Heater | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | N/A | STD | Honeywell Burst Sensor BES-EX
31 | GS-103 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | Air Heater | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | N/A | STD | Honeywell Burst Sensor BES-EX
32 | GS-104 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | Air Heater | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | N/A | STD | Honeywell Burst Sensor BES-EX
33 | GS-105 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | Air Heater | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | N/A | STD | Honeywell Burst Sensor BES-EX
34 | XS-101 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
35 | XS-102 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
36 | XS-103 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
37 | XS-104 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
38 | XS-105 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
39 | XS-106 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | Dryer Duct | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
40 | GS-B6200 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6200 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
41 | GS-H6202 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | H6202 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
42 | GS-H6203 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | H6203 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
43 | GS-H6204 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | H6204 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
44 | GS-B6506 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6506 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
45 | GS-B6507 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6507 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
46 | GS-B6508 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6508 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
47 | GS-B6509 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6509 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
48 | GS-B6510 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6510 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
49 | GS-B6511 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | B6511 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
50 | GS-B6512 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | B6512 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
51 | XS-F6506 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6506 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
52 | XS-F6507 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6507 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
53 | XS-F6508 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6508 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
54 | XS-F6509 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6509 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
55 | XS-F6510 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6510 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
56 | XS-F6511 | 1 | Burst Sensor | Common Area | Explosion Hatch | Hot Air | F6511 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
57 | XS-B6512 | 1 | Burst Sensor | Common Area | Explosion Vent | Hot Air | B6512 | – | Burst Sensor | Safety | DI | Hot Air + Starch |  |  |  |  | G/S | Mounted | – | – | Contact |  | On/Off | – | [12 empty] | Honeywell | Zone 20 | STD | Honeywell Burst Sensor BES-EX
58 | LSH-B6506 | 1 | Instrument | Common Area | – | Starch Collecting Hopper A | B6506 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1 | FTM50: standard Aschach EN10226 R1-1/2, FEM52; 3-wire PNP 10-55VDC
59 | LSH-B6507 | 1 | Instrument | Common Area | – | Starch Collecting Hopper B | B6507 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
60 | LSH-B6508 | 1 | Instrument | Common Area | – | Starch Collecting Hopper C | B6508 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
61 | LSH-B6509 | 1 | Instrument | Common Area | – | Starch Collecting Hopper D | B6509 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
62 | LSH-B6510 | 1 | Instrument | Common Area | – | Starch Collecting Hopper E | B6510 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
63 | LSH-B6511 | 1 | Instrument | Common Area | – | Starch Collecting Hopper F | B6511 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
64 | LSL-B6512 | 1 | Instrument | Common Area | – | Starch Silo | B6512 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
65 | LSH-B6512 | 1 | Instrument | Common Area | – | Starch Silo | B6512 | – | Level Switch | Vib. Fork | DI | Dry Starch | Amb. |  | 80 |  | S | 3/4" NPT | – | 24 VDC | NO |  | On/Off | – | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | E + H | Zone 20 | FTM50 | FTM50-AA21A1
66 | MT-101 | 1 | Instrument | Common Area | – | Starch Silo Airlock | H6514 | – | Moisture Transmitter | Moisture TX | AI | Starch Moisture | 55 |  | 80 |  | S | Mounted | – | 4–20 mA | 4-20 mA |  | 0-50 | % | ACTIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | Perton | Zone 22 | STD | Perten AM5200-ATEX
67 | TG-103 | 1 | Instrument | Common Area | V6515 Inlet Duct | Hot Air | – | – | Temperature Gauge | Temperature Gauge | – | Hot Air | 50-170 |  | 200 |  | G | Mounted | Yes | – | Local |  | 0 - 200 | °C | PASSIVE | [10 empty] | SS 316L | EU | Zone 22 | Bimetal | Bimetal 0–200°C
68 | TT-103 | 1 | Instrument | Common Area | V6515 Inlet Duct | Hot Air | – | – | Temperature Transmitter |  | – | Hot Air | 50-170 | 0-1 | 200 | 2 | G | Threaded | Yes | Loop | 4–20 mA |  | 0 - 200 | °C | PASSIVE |  |  |  | FLD | CR | [5 empty] | SS 316L | EU | Zone 22 | RTD + TX | TMT182B-AAA1A1AA1B
69 | PG-103 | 1 | Instrument | Common Area | V6515 Inlet Duct | Hot Air | – | – | Pressure Gauge | Pressure Gauge | – | Hot Air | 50-170 | 0-1 | 200 | 2 | G | Threaded | – | – | Local |  | 0 - 2 | barg | PASSIVE | [10 empty] | SS 316L | WIKA | Zone 22 | Bourdon | WIKA 213.53 SS316
70 | PT-103 | 1 | Instrument | Common Area | V6515 Inlet Duct | Hot Air | – | – | Pressure Transmitter |  | AI | Hot Air | 50-170 | 0-1 | 200 | 2 | G | 1/2" NPT | – | Loop | 4–20 mA |  | 0 - 2 | barg | PASSIVE |  |  |  | FLD | CR | [6 empty] | EU | Zone 22 | STD | PMC51B-AA21A2B1A | Deltabar PMD78B: standard in Aschach with graph. Display
71 | TT-V6515A | 1 | Instrument | Common Area | – | V6515 Motor Temperature | V6515 | – | Temperature Transmitter |  | – | – | 50-80 |  | 200 |  | – | Inserted | – | – | RTD |  | 0 - 200 | °C | PASSIVE |  |  |  | MCC | CR | [6 empty] | E + H | Zone 22 | TR10 | iTEMP TMR31-A11ABACBFAB-1A0CA**
72 | TT-V6515B | 1 | Instrument | Common Area | – | V6515 Motor Temperature | V6515 | – | Temperature Transmitter |  | – | – | 50-80 |  | 200 |  | – | Inserted | – | – | RTD |  | 0 - 200 | °C | PASSIVE |  |  |  | MCC | CR | [6 empty] | E + H | Zone 22 | TR10 | iTEMP TMR31-A11ABACBFAB-1A0CA**
73 | TT-V6515C | 1 | Instrument | Common Area | – | V6515 Bearing Temperature | V6515 | – | Temperature Transmitter |  | – | – | 50-80 |  | 200 |  | – | Inserted | – | – | RTD |  | 0 - 200 | °C | PASSIVE |  |  |  | MCC | CR | [6 empty] | E + H | Zone 22 | TR10 | iTEMP TMR31-A11ABACBFAB-1A0CA**
74 | TT-V6515D | 1 | Instrument | Common Area | – | V6515 Bearing Temperature | V6515 | – | Temperature Transmitter |  | – | – | 50-80 |  | 200 |  | – | Inserted | – | – | RTD |  | 0 - 200 | °C | PASSIVE |  |  |  | MCC | CR | [6 empty] | E + H | Zone 22 | TR10 | iTEMP TMR31-A11ABACBFAB-1A0CA**
75 | VT-V6515 | 1 | Instrument | Common Area | – | V6515 Vibration | V6515 | – | Vibration Transmitter | Vibration TX | AI | – |  |  |  |  | – | Mounted | – | 24 DC | 4-20 mA |  | Vendor | mm/s | ACTIVE |  |  |  | FLD | [7 empty] | EU | Zone 22 | STD | IFM VSA003-ATEX
76 | VFD-M1 | 1 | VFD | – |  | B6200 Motor VFD | B6200 | – | – | Continuous Command to VFD of B6200 | AO | – |  |  |  |  | – |  | – | 24 DC | 4-20 mA |  | – | – | ACTIVE |  |  |  | CR | MCC | [6 empty] | ABB/Siemens | N/A | STD | ABB ACS580/ACS880 / Siemens VFD – Vendor Std | VFDs --> ABB ACS580/ACS880
77 | VFD-M4 | 1 | VFD | – |  | H6204 Motor VFD | H6204 | – | – | Continuous Command to VFD of H6204 | AO | – |  |  |  |  | – |  | – | 24 DC | 4-20 mA |  | – | – | ACTIVE |  |  |  | CR | MCC | [6 empty] | ABB/Siemens | Zone 22 | STD | ABB ACS580/ACS880 / Siemens VFD – Vendor Std
78 | VFD-M6 | 1 | VFD | – |  | H6514 Motor VFD | H6514 | – | – | Continuous Command to VFD of H6514 | AO | – |  |  |  |  | – |  | – | 24 DC | 4-20 mA |  | – | – | ACTIVE |  |  |  | CR | MCC | [6 empty] | ABB/Siemens | Zone 22 | STD | ABB ACS580/ACS880 / Siemens VFD – Vendor Std
79 | VFD-M8 | 1 | VFD | – |  | B6515 Motor VFD | B6515 | – | – | Continuous Command to VFD of V6515 | AO | – |  |  |  |  | – |  | – | 24 DC | 4-20 mA |  | – | – | ACTIVE |  |  |  | CR | MCC | [6 empty] | ABB/Siemens | Zone 22 | STD | ABB ACS580/ACS880 / Siemens VFD – Vendor Std
80 | ST-M1 | 1 | Shaft Speed | – |  | B6200 Motor Shaft Speed | B6200 | – | – | [7 empty] | – |  | – | [18 empty] | N/A
81 | ST-M2 | 1 | Shaft Speed | – |  | R6201 Motor Shaft Speed | R6201 | – | – | [7 empty] | – |  | – | [18 empty] | N/A
82 | ST-M3 | 1 | Shaft Speed | – |  | H6202 Motor Shaft Speed | H6202 | – | – | [7 empty] | – |  | – | [18 empty] | N/A
83 | ST-M4 | 1 | Shaft Speed | – |  | H6203 Motor Shaft Speed | H6203 | – | – | [7 empty] | – |  | – | [18 empty] | Zone 22
84 | ST-M5 | 1 | Shaft Speed | – |  | H6204 Motor Shaft Speed | H6204 | – | – | [7 empty] | – |  | – | [18 empty] | Zone 22
85 | ST-M6 | 1 | Shaft Speed | – |  | H6514 Motor Shaft Speed | H6514 | – | – | [7 empty] | – |  | – | [18 empty] | Zone 22
86 | ST-M7 | 1 | Shaft Speed | – |  | H6513 Motor Shaft Speed | H6513 | – | – | [7 empty] | – |  | – | [18 empty] | Zone 22
Process connection "Mounted" means?
Perten DA7430M: datasheet not found, not checked
Cable glands M20 not NPT, ...
NJ1.5-8GM-N: 8mm okay
Material/test certificates are not included (EN 10204) - to be discussed e.g. for FT S101, ... are there any SIL requirements?
The suitability of the equipment for use in hygiene areas (as far as applicable) e. g. process connection has to be checked!
ATEX requirements - To be updated after Ex. Zoning plan.
Note on Y22: Administrator: Shall be specified by BODA
Note on C23: Administrator: All Data Shall be specified by BODA
Note on C24: Administrator: All data Shall be specified by BODA
Note on C26: Administrator: All Data Shall be specified by BODA
Note on C29: Administrator: All data Shall be Specified
Note on C30: Administrator: All data shall be Specified
Note on C31: Administrator: All data shall be specified
Note on C32: Administrator: All data shall be specified
Note on C76: Administrator: All Data Shall Be Specified By BODA