CONTROL STRATEGY & CONTROL PHILOSOPHY

Flash Dryer System – Modified Starch

1. PURPOSE AND SCOPE

This document defines the complete Control Strategy and Control Philosophy for the Modified Starch Flash Dryer system, based on the approved P&ID (5204-PR-DW-0001-02).

, explosion protection layout, rotating equipment monitoring, and expert operational comments.

The philosophy covers:

- Process control

- Equipment protection

- Explosion and mechanical safety interfaces

- Startup, shutdown, and emergency logic

- Instrumentation usage and redundancy

- Operator interaction philosophy

2. OVERALL CONTROL OBJECTIVES

The primary control objectives of the Flash Dryer system are:

- Maintain final product moisture within specification.

- Prevent product overheating and degradation.

- Ensure continuous, stable solids conveying through the dryer.

- Protect rotating and pressurized equipment.

- Provide immediate safe response to explosion or mechanical failure.

- Ensure compliance with ATEX / EN 14491 explosion protection requirements.

3. CONTROL SYSTEM ARCHITECTURE

- Control platform: PLC

- Control layers:

  - Regulatory control (PID / PI)

  - Sequential control (step-based logic)

  - Interlock and trip layer

  - Operator HMI supervision

- Safety philosophy:

  - Hard interlocks in PLC

  - Fail-safe field devices

  - Interface with explosion protection devices

4. OPERATING MODES

| Mode | Description |
| --- | --- |
| OFF | All equipment de-energized |
| START-UP | Automatic controlled startup sequence |
| NORMAL OPERATION | Fully automatic cascade-controlled drying |
| SHUTDOWN | Controlled drying and cooldown |
| EMERGENCY SHUTDOWN | Immediate protective shutdown |
| MAINTENANCE | Local / manual control with interlocks enforced |

5. MAIN PROCESS CONTROL STRATEGY

5.1 Moisture-Based Cascade Control

The flash dryer operates under a cascade control strategy:

- Master controller: Online product moisture analyzer

- Slave controller: Exhaust air temperature controller

- Manipulated variable: Steam control valve to air heater

Control logic:

- The moisture controller adjusts the setpoint of exhaust air temperature.

- The temperature controller regulates steam flow to maintain that setpoint.

- If the moisture analyzer fails, the system automatically reverts to temperature-only control.

6. AIR SYSTEM AND FAN CONTROL

6.1 Dryer Fan Control (V6515)

Based on the P&ID, (5204-PR-DW-0001-02) the dryer fan is equipped with:

- VFD control

- Shaft speed measurement

- Bearing temperature monitoring

- Vibration monitoring

- Air velocity measurement at duct outlet

Control strategy:

- Fan speed is controlled to maintain required air velocity.

- Fan cannot start unless:

  - All downstream paths are open

  - Explosion vents are healthy

  - No active trip conditions exist

6.2 Fan Protection Interlocks

| Protection | Action |
| --- | --- |
| High bearing temperature | Fan trip |
| High vibration | Fan trip |
| Overspeed | VFD trip |
| Loss of airflow | Heater trip ((TCV- S101) |
| Shaft speed mismatch | Alarm then trip |

7. FEED SYSTEM CONTROL (STARCH CAKE FEEDER)

- Feed screw / feeder operates under mass measuring (WIC-B6200) control.

- Feed rate is interlocked with:

  - Fan running status

  - Heater availability

  - Cyclone and discharge readiness

If airflow or heating is lost:

- Feed is stopped immediately

- Purge sequence is initiated if allowed

8. HEATER AND STEAM CONTROL PHILOSOPHY

- Steam flow is modulated via control valve.

- Heater enable is permitted only if:

  - Fan is running

  - Minimum airflow is confirmed

  - No high temperature trip is active

Trips:

- High inlet air temperature (TIC-101) → Steam valve closed

- Fan trip → Steam valve closed (TCV- S101)

- Explosion signal → Steam valve closed

9. EXPLOSION PROTECTION AND BURST SENSOR LOGIC

9.1 Explosion Detection

The system includes multiple Burst Sensors XS-101 to XS-106 (Dryer Duct) + XS-F6506 to XS-F6511 (Cyclones) + XS-B6512 (Silo)) Installed on:

- Dryer duct

- Cyclone inlets

- Dry starch receiving silo

9.2 Explosion Response Strategy

Upon detection of burst / explosion signal:

Immediate actions:

- Close steam control valve )TCV- S101& TCV- S102).

- Stop product feed.

- Maintain fan operation if mechanically allowed (post-explosion purge).

- Generate latched alarm requiring manual reset.

Explosion events are treated as:

- Non-auto-resettable trips

- Root-cause investigation mandatory before restart

10. CYCLONE AND SOLIDS DISCHARGE CONTROL

- Cyclone discharge is via airlock/rotary valve.

- Rotary valves are interlocked with:

  - Fan operation

  - Cyclone pressure balance (controlled by level switches)

- Blockage detection results in:

  - Feed reduction

  - Alarm escalation

  - Controlled shutdown if unresolved

11. START-UP SEQUENCE (SUMMARY)

- System permissive check.

- Start dryer fan and verify airflow.

- Enable heater and warm-up.

- Start feed at minimum rate.

- Enable cascade moisture control.

- Ramp to normal production.

12. NORMAL SHUTDOWN SEQUENCE

- Stop feed.

- Continue drying until duct moisture clears.

- Disable heater.

- Cool-down with air.

- Stop fan.

13. EMERGENCY SHUTDOWN (ESD)

Triggers:

- Emergency stop

- Explosion signal

- Fan trip

- Critical temperature or vibration

Actions:

- Immediate steam isolation

- Immediate feed stops

- Fan logic based on structural integrity status

14. ALARM PHILOSOPHY

- First-out alarm logic applied

- Priority-based alarms:

  - High: Safety / equipment damage

  - Medium: Process deviation

  - Low: Advisory

- All trips require manual reset

15. INTERFACE WITH MECHANICAL DESIGN

The control philosophy is directly aligned with:

- Explosion vent sizing and location

- Vacuum design limits

- Mechanical stress limits of ducting and cyclones

- Fan operating envelope

No control action allows operation beyond mechanical design limits.

In the following, we describe the dryer control philosophy in three steps.

STEP 1 – CAUSE & EFFECT MATRIX

1. PURPOSE OF CAUSE & EFFECT MATRIX

This Cause & Effect Matrix defines the automatic protective and control responses of the Flash Dryer system to abnormal process, mechanical, or safety events.

The matrix ensures:

- Consistent and predictable system behavior

- Protection of personnel and equipment

- Compliance with explosion safety standards

- Clear implementation guidance for PLC/DCS programming

2. PHILOSOPHY AND DESIGN BASIS

- All Trips are latched and require manual reset.

- Explosion-related causes have highest priority.

- Steam isolation is always fail-safe closed.

- Feed stoppage is immediate on loss of safe drying conditions.

- Fan operation after trip depends on mechanical integrity and explosion logic.

3. Cause & Effect Matrix

| Symbol | Meaning | Description |
| --- | --- | --- |
| ✔ | Action Executed | The specified action is automatically executed when the cause occurs |
| — | No Action | No automatic action is initiated |
| L | Latched Trip | A trip that remains active until manually reset by the operator after fault clearance and, where applicable, completion of maintenance or safety inspection |
| A | Alarm Only | An operator alarm without automatic shutdown or trip action; the process may continue to operate within safe limits |

4. CAUSE & EFFECT MATRIX – MAIN PROCESS & SAFETY

4.1 Explosion & Fire Related Events

| Cause | Feed Stop | Steam Valve Close | Fan Stop | Fan Continue (Purge) | Alarm | Trip |
| --- | --- | --- | --- | --- | --- | --- |
| Burst Sensor – Dryer Duct | ✔ | ✔ | — | ✔ | ✔ | L |
| Burst Sensor – Cyclone Body | ✔ | ✔ | — | ✔ | ✔ | L |
| Burst Sensor – Exhaust Duct | ✔ | ✔ | — | ✔ | ✔ | L |
| Fire Detection (If Any) | ✔ | ✔ | ✔ | — | ✔ | L |

Notes:

- Fan continues only if mechanical integrity is confirmed.

- Restart requires inspection and manual reset.

4.2 Air System & Fan Protection

| Cause | Feed Stop | Steam Close | Fan Trip | Alarm | Trip |
| --- | --- | --- | --- | --- | --- |
| Fan Bearing High Temperature | ✔ | ✔ | ✔ | ✔ | L |
| Fan High Vibration | ✔ | ✔ | ✔ | ✔ | L |
| Fan Overspeed | ✔ | ✔ | ✔ | ✔ | L |
| Fan Motor Trip | ✔ | ✔ | ✔ | ✔ | L |
| Low Air Velocity in Duct | ✔ | ✔ | — | ✔ | A |

4.3 Heater & Temperature Protection

| Cause | Feed Stop | Steam Close | Fan Stop | Alarm | Trip |
| --- | --- | --- | --- | --- | --- |
| High Inlet Air Temperature | ✔ | ✔ | — | ✔ | L |
| High Exhaust Air Temperature | ✔ | ✔ | — | ✔ | L |
| Steam Supply Failure | ✔ | ✔ | — | ✔ | A |
| Condensate Backup High Level | ✔ | ✔ | — | ✔ | L |

4.4 Feed System Abnormal Conditions

| Cause | Feed Stop | Steam Close | Fan Stop | Alarm | Trip |
| --- | --- | --- | --- | --- | --- |
| Feeder Motor Trip | ✔ | — | — | ✔ | A |
| Feed Blockage | ✔ | — | — | ✔ | A |
| Loss of Airlock Rotation | ✔ | — | — | ✔ | L |

4.5 Cyclone & Solids Discharge

| Cause | Feed Stop | Steam Close | Fan Stop | Alarm | Trip |
| --- | --- | --- | --- | --- | --- |
| Cyclone High Differential Pressure | ✔ | — | — | ✔ | A |
| Rotary Valve Failure | ✔ | — | — | ✔ | L |
| Solids Backup High Level | ✔ | — | — | ✔ | L |

4.6 Instrument & Control System Failures

| Cause | Control Mode Change | Feed Stop | Alarm |
| --- | --- | --- | --- |
| Online Moisture Analyzer Failure | Temp Control Only | — | ✔ |
| Exhaust Temp Sensor Failure | Safe Steam Close | ✔ | ✔ |
| PLC / DCS CPU Fault | All Outputs Safe | ✔ | ✔ |

5. RESET AND RESTART PHILOSOPHY

- Explosion-related trips cannot be auto-reset.

- Mechanical trips require maintenance clearance.

- Restart sequence must follow defined startup logic.

- First-out alarm is retained for diagnostics.

STEP 2 – DETAILED OPERATING SEQUENCES

Start-up, Normal Shutdown & Emergency Shutdown

1. PURPOSE OF THIS SECTION

This section provides a detailed, step-by-step operational description of:

- Start-up sequence

- Normal shutdown sequence

- Emergency shutdown sequence

The intent is to ensure:

- Safe and repeatable operation

- Clear understanding for operators and commissioning engineers

- Direct traceability to control logic and interlocks

2. GENERAL SEQUENCE PHILOSOPHY

- All sequences are executed automatically in AUTO mode.

- Each step requires defined entry conditions, actions, and exit conditions.

- Any critical trip overrides the active sequence and forces emergency logic.

- Operators can observe but not bypass sequence steps.

3. DETAILED START-UP SEQUENCE (AUTO MODE)

STEP SU-00 – System Standby

System State:

- All drives stopped

- Steam valve closed

- No active trips

- System in AUTO mode

Operator Action:

- Press “Start Flash Dryer” command

STEP SU-10 – Pre-Start Safety and Permissive Check

Control Actions:

- Verify all emergency stops are reset

- Confirm no explosion or fire trips active

- Check availability of:

  - Dryer fan

  - Steam supply

  - Condensate removal

  - Cyclones and rotary valves

- Verify instrument health (temperature, airflow, vibration)

If any permissive is not satisfied:

- Sequence is held

- Operator alarm generated

Exit Condition:

- All permissive = TRUE

STEP SU-20 – Dryer Fan Start and Stabilization

Control Actions:

- Start dryer fan via VFD

- Monitor:

  - Fan shaft speed

  - Bearing temperatures

  - Vibration levels

  - Air velocity in main duct

Interlocks:

- Heater and feed remain disabled

Exit Condition:

- Air velocity ≥ minimum design value (e.g. 22 m/s)

- Fan parameters stable for defined time

STEP SU-30 – Heater Warm-Up Phase

Control Actions:

- Enable steam control valve

- Ramp inlet air temperature to warm-up setpoint

- Monitor exhaust air temperature

Protection:

- High temperature limits enforced

- Steam closed immediately on fan fault

Exit Condition:

- Exhaust air temperature reaches minimum drying threshold

STEP SU-40 – Feed System Initiation (Low Load)

Control Actions:

- Start rotary valves / airlocks

- Start feed system at minimum feed rate

- Maintain stable air temperature

Monitoring:

- Cyclone pressure balance

- Solids discharge continuity

Exit Condition:

- Stable exhaust temperature

- No abnormal vibration or pressure

STEP SU-50 – Ramp-Up to Normal Operation

Control Actions:

- Enable moisture-based cascade control

- Gradually ramp feed rate to production target

- Allow exhaust temperature setpoint to be adjusted by moisture controller

System State:

- Normal automatic operation achieved

4. NORMAL OPERATION MONITORING

During normal operation, the system continuously monitors:

- Product moisture

- Exhaust air temperature

- Air velocity

- Fan vibration and bearing temperature

- Cyclone pressure and discharge status

Any deviation results in alarms or controlled corrective action.

5. NORMAL SHUTDOWN SEQUENCE (CONTROLLED STOP)

STEP SD-10 – Feed Stop

Trigger:

- Operator stop command

Control Actions:

- Stop product feed immediately

- Maintain airflow and heating

STEP SD-20 – Drying and Duct Clearing Phase

Control Actions:

- Continue fan operation

- Maintain exhaust air temperature

- Allow remaining product to fully exit dryer and cyclones

Exit Condition:

- No solids detected in system

- Stable exhaust conditions

STEP SD-30 – Heater Shutdown

Control Actions:

- Close steam control valve

- Maintain airflow for cooldown

STEP SD-40 – Fan Cooldown and Stop

Control Actions:

- Continue fan until system temperature decreases to safe level

- Stop fan

- System returns to standby

6. EMERGENCY SHUTDOWN SEQUENCE (ESD)

6.1 Emergency Shutdown Triggers

Emergency shutdown is initiated by any of the following:

- Explosion / burst sensor activation

- Emergency stop pushbutton

- Fan critical trip (vibration, bearing temperature, overspeed)

- Heater critical overtemperature

6.2 Emergency Shutdown Actions (Immediate)

Upon ESD trigger, the following actions occur without delay:

- Steam control valve closes (fail-safe)

- Product feed stops

- Moisture and temperature control loops disabled

- Emergency alarms generated and latched

6.3 Fan Operation During Emergency

- If explosion detection is active:

  - Fan operation follows explosion venting and purge philosophy

- If mechanical trip:

  - Fan is stopped immediately

Fan behavior is defined by mechanical integrity status.

6.4 Post-Emergency State

- System remains locked in ESD state

- Manual inspection and clearance required

- Full start-up sequence mandatory for restart

7. SEQUENCE INTERRUPTION AND RECOVERY

- Any trip interrupts the active sequence.

- After fault clearance:

  - Operator must reset trips

  - System returns to STEP SU-00

- Partial sequence restart is not permitted.

8. INTERLOCK AND TRIP LOGIC (PSEUDO CODE)

8.1 Heater Enable Interlock

IF Fan Running = TRUE

AND Airflow_OK = TRUE

AND No_Active_Trips = TRUE

THEN

Heater_Enable = TRUE

ELSE

Heater_Enable = FALSE

END_IF

8.2 Feed Enable Interlock

IF Fan_Running = TRUE

AND Heater_Enabled = TRUE

AND Exhaust_Temp_Stable = TRUE

AND Explosion_OK = TRUE

THEN

Feed_Enable = TRUE

ELSE

Feed_Enable = FALSE

END_IF

8.3 Explosion Trip Logic

IF Burst_Sensor_Activated = TRUE

THEN

Steam_Valve = CLOSE

Feed_Enable = FALSE

Explosion_Trip = TRUE

Alarm_Latched = TRUE

END_IF

8.4 Fan Protection Logic

IF Bearing_Temp_High OR Vibration_High OR Overspeed

THEN

Fan_Trip = TRUE

Steam_Valve = CLOSE

Feed_Enable = FALSE

END_IF

8.5 Moisture Analyzer Failure Logic

IF Moisture_Analyzer_Fault = TRUE

THEN

Moisture_Control = DISABLED

Exhaust_Temp_Control = ENABLED

Alarm = TRUE

END_IF

STEP 3 – ALARM, TRIP & OPERATOR ACTION PHILOSOPHY

1. PURPOSE OF THIS SECTION

This section defines the alarm and trip philosophy of the Flash Dryer system, including:

- Classification of alarms and trips

- Process rationale behind each protection

- Expected operator actions

- Clear distinction between alarms and shutdown events

The objective is to:

- Prevent unsafe operating conditions

- Protect equipment and product quality

- Avoid nuisance alarms

- Support efficient operator response

2. GENERAL ALARM PHILOSOPHY

2.1 Alarm Design Principles

- Alarms are generated only when operator action is required.

- Alarms are prioritized according to process risk.

- Alarms do not automatically stop the plant, unless escalated to a trip.

- Each alarm has:

  - Clear cause

  - Clear consequence

  - Defined operator response

2.2 Alarm Priority Classification

| Priority | Description | Operator Response Time |
| --- | --- | --- |
| High (H) | Immediate risk to safety or equipment | Immediate |
| Medium (M) | Risk to process stability or quality | Short term |
| Low (L) | Advisory or maintenance-related | When convenient |

3. GENERAL TRIP PHILOSOPHY

- Trips result in automatic shutdown actions.

- Trips are latched and require manual reset.

- Trips override all operating modes.

- Explosion and fire-related trips have the highest priority.

- Trips always act in a fail-safe manner.

4. ALARM & TRIP CLASSIFICATION BY PROCESS AREA

4.1 Air System and Fan Protection

Alarms

| Alarm | Priority | Process Meaning | Operator Action |
| --- | --- | --- | --- |
| Low Air Velocity | M | Risk of poor entrainment | Monitor, prepare for load reduction |
| Fan Bearing Temperature High | H | Mechanical degradation | Reduce load, prepare for shutdown |
| Fan Vibration High (Warning) | M | Early mechanical issue | Inform maintenance |

Trips

| Trip | Process Action |
| --- | --- |
| Fan Bearing Temperature High-High | Fan stop, steam close, feed stop |
| Fan Vibration High-High | Fan stop, steam close, feed stop |
| Fan Overspeed | Immediate fan trip |

4.2 Heater and Thermal Protection

Alarms

| Alarm | Priority | Meaning |
| --- | --- | --- |
| Inlet Air Temperature High | H | Heater overload |
| Exhaust Air Temperature High | H | Product overheating risk |
| Condensate Level High | M | Heater efficiency loss |

Trips

| Trip | Process Action |
| --- | --- |
| Heater Overtemperature | Steam valve close |
| Condensate High-High | Steam valve close |
| Steam Supply Failure (Critical) | Controlled feed stop |

4.3 Product Quality and Drying Performance

Alarms

| Alarm | Priority | Meaning |
| --- | --- | --- |
| Product Moisture High | M | Under-drying |
| Product Moisture Low | M | Over-drying |
| Moisture Analyzer Fault | M | Loss of quality feedback |

Control Response (No Trip)

- Switch to exhaust temperature control

- Operator informed

- Production may continue at reduced performance

4.4 Feed System and Solids Handling

Alarms

| Alarm | Priority | Meaning |
| --- | --- | --- |
| Feed Blockage | M | Risk of unstable drying |
| Rotary Valve Speed Low | M | Solids backup risk |
| Cyclone Differential Pressure High | M | Fouling or overload |

Trips

| Trip | Process Action |
| --- | --- |
| Rotary Valve Failure | Feed stop |
| Solids High Level | Feed stop |

4.5 Explosion and Fire Protection

Trips (Highest Priority)

| Cause | Automatic Actions |
| --- | --- |
| Explosion / Burst Sensor Activation | Steam close, feed stop, alarms latched |
| Fire Detection | Steam close, feed stop, fan logic per design |
| Emergency Stop | Immediate ESD |

Notes:

- Explosion-related trips are never bypassed.

- Restart requires mechanical inspection and management approval.

5. FIRST-OUT ALARM PHILOSOPHY

- The first detected trip or alarm is recorded as First-Out.

- Subsequent alarms are logged but do not mask the root cause.

- First-Out indication is clearly displayed to operators.

6. OPERATOR RESPONSE GUIDELINES

Alarm Response

Operators are expected to:

- Identify alarm priority

- Assess process trend

- Take corrective action

- Escalate to shut down if alarm persists

Trip Response

Operators must:

- Acknowledge trip

- Secure the system

- Inform maintenance and supervision

- Perform inspection

- Reset only after clearance

7. ALARM RATIONALISATION PHILOSOPHY

- Each alarm is justified by a process risk.

- Duplicate alarms are avoided.

- Alarm limits are aligned with:

  - Equipment design limits

  - Product quality constraints

  - Safety margins

8. INTERFACE WITH FAT / SAT

During FAT and SAT:

- All alarms are tested for correct priority and message

- Trips are verified for correct actions

- Operator displays are validated for clarity