# FLASH DRYER

## COMPREHENSIVE CONTROL STRATEGY

TABLE OF CONTENT

1. Primary Control Loops3

2. Safety Interlocks & ESD System 5

3. Sequence Control7

4. Monitoring & DATA Acquisition 9

5. Additional Control Strategies11

6. Control System Architecture 12

7. Implementation Priority13

8. Key Performance Indicators14

## 1.PRIMARY CONTROL LOOPS

### 1.1. MAIN MOISTURE CONTROL LOOP (Cascade Control)

Primary Loop - Moisture Control:

- Sensor: MT-101 (Moisture Transmitter, 0-50% range)

- Controller: MIC-101 (Moisture Indicating Controller)

- Setpoint: 12% moisture (adjustable based on product specification)

- Output: Setpoint to secondary temperature loop

Secondary Loop - Temperature Control:

- Sensor: TT-103 (Temperature Transmitter at Fan Inlet, 0-200°C)

- Controller: TIC-103 (Temperature Indicating Controller)

- Setpoint: Received from MIC-101 (typically 60-80°C)

- Output: 4-20mA to Steam Control Valve on Zone 3 Heater (TCV-101)

Control Algorithm:

IF MT-101 > Setpoint THEN

Decrease TIC-103 Setpoint (reduce drying temperature)

ELSE IF MT-101 < Setpoint THEN

Increase TIC-103 Setpoint (increase drying temperature)

ENDIF

### 1.2. FEED RATE CONTROL BASED ON MOISTURE

### Control Logic: In normal operation, moisture control is performed by the 1.1. MAIN MOISTURE CONTROL LOOP (Cascade Control) until the deviation from the setpoint becomes significant or sudden changes occur in the conditions of the input cake to the dryer; at that point, the control of the dryer is assigned to this loop (1.2. FEED RATE CONTROL BASED ON MOISTURE) until conditions stabilize.

- Master: MT-101 Moisture reading

- Slave: VFD-B6200 (Agitated Feed Vessel speed)

- WT-B6200: Weight measurement for feed rate calculation

Feed Rate Adjustment = f(MT-101, Product Throughput)

IF MT-101 > 15% THEN

Reduce VFD-B6200 speed by 10%

ELSE IF MT-101 < 9% THEN

Increase VFD-B6200 speed by 10%

ENDIF

### 1.3. SECONDARY TEMPERATURE CONTROL LOOP

After-Heater Temperature Control:

- Sensor: TT-102 (Temperature Transmitter in Dryer Duct, 0-200°C)

- Controller: TIC-102 (Temperature Controller)

- Setpoint: 170°C (adjustable)

- Alarms:

  - TAH-102: High Alarm at 180°C

  - TAL-102: Low Alarm at 150 ((variable based on capacity))

- Output: Trim adjustment to main steam valve

Safety Interlock:

IF TT-102 > 185°C THEN

Close steam valve fully

Activate emergency stop sequence

ENDIF

## 2. SAFETY INTERLOCKS & ESD SYSTEM

### 2.1. EXPLOSION PROTECTION SYSTEM

Sensors: XS-101 to XS-106 (Dryer Duct) + XS-F6506 to XS-F6511 (Cyclones) + XS-B6512 (Silo)

IF ANY explosion sensor activated THEN

IMMEDIATE:

1. Close all steam valves (FT-S101 related)

2. Stop ID fan (V6515)

3. Stop the starch cake feed system to the dryer, including screw conveyors M-1      to M-4 and the starch cake blower (H6204).

4. Activate quench steam suppression system

5. Isolate system from plant

6. Alarm to control room

ENDIF

### 2.2. HIGH TEMPERATURE PROTECTION

IF TT-101 > 180°C OR TT-102 > 185°C THEN

Close steam control valve

Reduce fan speed to 50%

Alarm: "HIGH TEMPERATURE - PROCESS INTERRUPTED"

ENDIF

### 2.3. PRESSURE SAFETY

text

IF PT-102 > 1.5 barg OR PT-103 < -0.5 barg THEN

Stop ID fan (V6515)

Open emergency vent

Alarm: "PRESSURE DEVIATION - SYSTEM STOPPED"

ENDIF

### 2.4. DOOR SAFETY INTERLOCKS

Sensors: GS-101 to GS-106 (Heater & Duct doors) + GS-B6200 to GS-H6512, GS-H6513 (Equipment access)

IF ANY door open during operation, THEN

Stop relevant equipment section

Prevent restart until door closed

Local indication + Control room alarm

ENDIF

## 3. SEQUENCE CONTROL

### 3.1. STARTUP SEQUENCE

PHASE 1: PRE-START CHECKS

- All doors closed (GS-xxx verification)

- No active alarms

- Utilities available (steam, power, air)

- Safety systems armed

PHASE 2: COLD START

1. Start exhaust fan V6515 at 20% speed

2. Open steam valve gradually to reach TT-A102 = 50°C

3. Start feed system (B6200 → H6202 → H6203 → H6204)

4. Ramp up fan speed to 50%

5. Increase temperature to setpoint (TT-102 = 170°C)

PHASE 3: NORMAL OPERATION

- Engage moisture control loop (MT-101 → TIC-103)

- Monitor all parameters

- Ramp to 100% capacity

### 3.2. NORMAL SHUTDOWN SEQUENCE

STEP 1: Feed system stop

- Stop B6200 (feed vessel) after WT-B6200 tend to Zero

- Stop H6202 (screw conveyor)+Delay Time

- Stop H6203 (feeder) +Delay Time

- Stop H6204 (wet blower) +Delay Time

STEP 2: Drying system cooldown

- Reduce steam valve to 10%

- Maintain fan at 30% for 10 minutes

- When TT-103 < 50°C, stop fan

STEP 3: Complete shutdown

- Close steam valve

- Isolate system

- Purge if necessary

### 3.3. EMERGENCY SHUTDOWN SEQUENCE

TRIGGERS:

- ESD button pressed

- Explosion detected (XS-xxx)

- Fire alarm

- Power failure

- Critical parameter deviation

ACTIONS:

IMMEDIATE (0-2 seconds):

1. Close all steam valves

2. Stop all rotating equipment

3. Activate suppression if needed

FOLLOW-UP (2-30 seconds):

4. Purge system with inert gas

5. Isolate from plant

6. Full system alarm

### 3.4. OPERATIONAL MODES

AUTO MODE:

- All control loops active

- Automatic startup/shutdown

- Recipe-based operation

MANUAL MODE:

- Operator control of individual devices

- Override capability

- For maintenance/troubleshooting

RECIPE MODE:

- Product-specific parameters

- Automatic adjustment for different starch types

- Historical data logging

## 4. MONITORING & DATA ACQUISITION

### 4.1. CRITICAL PARAMETERS MONITORING

TEMPERATURES (All TT-xxx):

- TT-S101: Steam header (0-220°C)

- TT-101: Dryer inlet (0-200°C)

- TT-102: Dryer process (0-200°C)

- TT-103: Fan inlet (0-200°C)

- TT-C101-C104: Condensate temperatures

PRESSURES (All PT-xxx & PG-xxx):

- PT-S101: Steam pressure (0-16 barg)

- PT-102/103: Process pressures (0-2 barg)

- Trend analysis for filter clogging detection

FLOW:

- FT-S101: Steam flow (0-xxx kg/hr)

- FT-C101: Condensate flow

MOISTURE:

- MT-101: Product moisture (0-50%)

### 4.2. EQUIPMENT STATUS MONITORING

MOTOR STATUS:

- V6515: Fan status, speed, vibration (VT-V6515)

- Temperature monitoring: TT-V6515A/B (motor), TT-V6515C/D (bearings)

ROTATING EQUIPMENT:

- Speed sensors ST-M1 to ST-M7

- Vibration monitoring for predictive maintenance

LEVEL MONITORING:

- LSH-B6506 to LSH-B6512: Hopper/silo high level

- LSL-B6512: Silo low level

- LT-B6515: Condensate tank level

### 4.3. ALARM MANAGEMENT

Priority 1 (Critical - Red):

- Explosion sensor activation

- Temperature > 185°C

- Motor failure

- Safety system fault

Priority 2 (High - Orange):

- Temperature deviation > 10°C

- Pressure deviation > 20%

- Moisture out of spec

- Level alarms

Priority 3 (Medium - Yellow):

- Equipment warning

- Maintenance due

- Efficiency drop

## 5. ADDITIONAL CONTROL STRATEGIES

### 5.1. ENERGY OPTIMIZATION

text

IF Condensate temperature (TT-C104) < 85°C THEN

Adjust steam trap operation

Optimize heat recovery

ENDIF

Fan speed optimization based on:

- Pressure drop across system (PT-102 to PT-103)

- Product moisture content

- Energy consumption

### 5.2. PRODUCT QUALITY ASSURANCE

text

Continuous monitoring:

- Moisture consistency (MT-101 trend)

- Temperature profile (TT-101, TT-102, TT-103)

- Residence time calculation

- Product throughput rate

### 5.3. PREVENTIVE MAINTENANCE TRIGGERS

text

Vibration monitoring (VT-V6515):

IF > 4.5 mm/s THEN Warning

IF > 7.0 mm/s THEN Alarm + Schedule maintenance

Bearing temperature (TT-V6515C/D):

IF > 85°C THEN Investigate

IF > 95°C THEN Schedule maintenance

## 6. CONTROL SYSTEM ARCHITECTURE

### 6.1. HARDWARE CONFIGURATION

PLC System:

- Redundant processors

- Distributed I/O stations

- Safety PLC for ESD functions

Field Devices:

- 4-20mA analog signals (majority)

- Digital inputs for status/interlocks

- Profibus/Profinet for smart devices

Human-Machine Interface:

- Redundant operator stations

- Engineering workstation

- Mobile access for maintenance

### 6.2. COMMUNICATION PROTOCOLS

- MODBUS TCP/IP for PLC to DCS

- PROFINET for field devices

- OPC UA for data historian

- Wireless for mobile devices

## 7. IMPLEMENTATION PRIORITY

PHASE 1 (Immediate - Safety):

- ESD system implementation

- Temperature safety interlocks

- Door safety interlocks

PHASE 2 (Short-term - Basic Control):

- Moisture-temperature cascade control

- Basic sequence control

- Critical parameter monitoring

PHASE 3 (Medium-term - Optimization):

- Advanced control algorithms

- Energy optimization

- Predictive maintenance

PHASE 4 (Long-term - Integration):

- Full plant integration

- Advanced analytics

- Remote monitoring

## 8. KEY PERFORMANCE INDICATORS

text

1. Product Moisture Consistency: ±0.5%

2. Energy Consumption: ≤0.608 ton steam/ton product

3. System Availability: >98%

4. Safety Incident Rate: 0

5. Maintenance Cost: <2% of CAPEX annually

This comprehensive control strategy ensures safe, efficient, and reliable operation of your modified starch drying system while meeting all your specified requirements and incorporating industry best practices.